## Current Draw Reference
ModuLaser Module Current Draw — Reference Table
18V figures per manufacturer worksheet; 24V figures as embedded in the ModuLaser Battery Calculator
Module Type | Model | 18V Current (mA) | 24V Current (mA) — as used by calculator
Minimum Display | FHSD8300-ULF | 242 | 210
Standard Display | FHSD8310-ULF | 266 | 232
Command Display | FHSD8320-ULF | 266 | 232
Detector (Fan Speed 1) | FHSD8330-ULF | 250 | 218
Detector (Fan Speed 2) | FHSD8330-ULF | 279 | 234
Detector (Fan Speed 3) | FHSD8330-ULF | 305 | 255
Detector (Fan Speed 4) | FHSD8330-ULF | 330 | 279
Detector (Fan Speed 5) | FHSD8330-ULF | 358 | 301
Detector (Fan Speed 6) | FHSD8330-ULF | 380 | 330
Detector (Fan Speed 7) | FHSD8330-ULF | 430 | 363
Detector (Fan Speed 8) | FHSD8330-ULF | 465 | 393
Detector (Fan Speed 9) | FHSD8330-ULF | 517 | 431
Detector (Fan Speed 10) | FHSD8330-ULF | 566 | 471
Detector (Fan Speed 11) | FHSD8330-ULF | 615 | 506
Detector (Fan Speed 12) | FHSD8330-ULF | 685 | 552
Detector (Fan Speed 13) | FHSD8330-ULF | 733 | 602
Detector (Fan Speed 14) | FHSD8330-ULF | 786 | 646
Detector (Fan Speed 15) | FHSD8330-ULF | 872 | 712
Detector (Fan Speed 16) | FHSD8330-ULF | 1021 | 762
MiniLaser ASD (standalone) — by Fan Speed
Module Type | Model | Standby (mA, 24 VDC) | Alarm (mA, 24 VDC) — as used by calculator
MiniLaser (Fan Speed 1) | FHSD8075-ULF | 120 | 120
MiniLaser (Fan Speed 2) | FHSD8075-ULF | 134 | 134
MiniLaser (Fan Speed 3) | FHSD8075-ULF | 157 | 157
MiniLaser (Fan Speed 4) | FHSD8075-ULF | 180 | 180
MiniLaser (Fan Speed 5) | FHSD8075-ULF | 200 | 200
MiniLaser (Fan Speed 6) | FHSD8075-ULF | 230 | 230
MiniLaser (Fan Speed 7) | FHSD8075-ULF | 255 | 255
MiniLaser (Fan Speed 8) | FHSD8075-ULF | 285 | 285
MiniLaser (Fan Speed 9) | FHSD8075-ULF | 320 | 320
MiniLaser (Fan Speed 10) | FHSD8075-ULF | 365 | 365
Notes:
• 18V figures shown are taken directly from the manufacturer's current-draw worksheet at the 18.0V test point ("New UL Values").
• 24V figures are the values embedded in the ModuLaser Battery Calculator, which do not match either the 18.0V or 20.4V rows in the manufacturer worksheet exactly — they reflect a separate reference point used when the calculator was built.
• Display rows are collapsed to a single current value each, per the calculator's own model (which does not distinguish TFT or LEDS state) — the TFT-On/LEDS-On (highest-draw) state was used to select the corresponding 18V figure. See cell comments on Minimum Display and Command Display for the two cases where that exact combination wasn't available in the source data and a documented substitution was made.
• MiniLaser (FHSD8075-ULF): current at 24 VDC from the MiniLaser Installation Manual; alarm draw = fan-speed draw (standby = alarm). No 18V figure is published for the MiniLaser. Each MiniLaser is on its own dedicated AUX circuit (35 mA per-circuit overhead, 3.0 A limit).
• MiniLaser I/O Expansion Module (9-30521) and Expansion Housing (9-30520): no current draw published; treated as no added draw (per Brent, 2026-10-16).